## SMALL BORE PIPES
WELDED
Steel Tubes For Uses in Water, Gas, Air And Steam
Conforming To Is : 1239 ( Part -1 ) 2004/BS : 1387/ 85
N. B. and Series mm | Outside Diameter |  | Wall Thckness |  | Nominal Weight Black Tubes |  |  |  | Noinal Weight Galv. Tubes |  |  |  | Socket
| Min | Max | mm | swg | Plain End |  | Screwe &Socked |  | Plain End |  | Screwe &Socked |  | Min -od | Max - Length
| mm | mm |  |  | kg/m | m/tonne | kg/m | m/tonne | kg/m | m/tonne | kg/m | m/tonne | mm | mm
15 L | 21 | 21.4 | 2 | 14 | 0.947 | 1056 | 0.956 | 1046 | 0.947 | 1056 | 0.956 | 1046 | 27 | 37
M | 21 | 21.8 | 2.6 | 12 | 1.21 | 826 | 1.22 | 819 | 1.21 | 826 | 1.22 | 819
H | 21 | 21.8 | 3.2 | 10 | 1.44 | 694 | 1.45 | 689 | 1.44 | 689 | 1.45 | 689
20 L | 26.4 | 26.9 | 2.3 | 13 | 1.38 | 724 | 1.39 | 719 | 1.38 | 719 | 1.39 | 719 | 32.5 | 39
M | 26.5 | 27.3 | 2.6 | 12 | 1.56 | 641 | 1.57 | 637 | 1.56 | 637 | 1.57 | 637
H | 26.5 | 27.3 | 3.2 | 10 | 1.87 | 534 | 1.88 | 532 | 1.87 | 532 | 1.88 | 532
25 L | 33.2 | 33.8 | 2.6 | 12 | 1.98 | 5.5 | 2 | 500 | 1.98 | 500 | 2 | 500 | 39.5 | 46
M | 33.3 | 34.2 | 3.2 | 10 | 2.41 | 415 | 2.43 | 411 | 2.41 | 411 | 2.43 | 411
H | 33.3 | 34.2 | 4 | 8 | 2.93 | 341 | 2.95 | 339 | 2.93 | 339 | 2.95 | 339
32 L | 41.9 | 42.5 | 2.6 | 12 | 2.54 | 393 | 2.57 | 389 | 2.54 | 389 | 2.57 | 389 | 49 | 51
M | 42 | 42.9 | 3.2 | 10 | 3.1 | 322 | 3.13 | 319 | 3.1 | 319 | 3.13 | 319
H | 42 | 42.9 | 4 | 8 | 3.79 | 264 | 3.82 | 261 | 3.79 | 261 | 3.82 | 261
40 L | 47.8 | 48.4 | 2.9 | 11 | 3.23 | 309 | 3.27 | 306 | 3.23 | 306 | 3.27 | 306 | 56 | 51
M | 47.9 | 48.8 | 3.2 | 10 | 3.56 | 281 | 3.6 | 277 | 3.56 | 277 | 3.6 | 277
H | 47.9 | 48.8 | 4 | 8 | 4.37 | 229 | 4.41 | 226 | 4.37 | 226 | 4.41 | 226
50 L | 59.6 | 60.2 | 2.9 | 11 | 4.08 | 245 | 4.15 | 241 | 4.08 | 241 | 4.15 | 241 | 68 | 60
M | 59.7 | 60.8 | 3.6 | 9 | 5.03 | 199 | 5.1 | 196 | 5.03 | 196 | 5.1 | 196
H | 59.7 | 60.8 | 4.5 | 7 | 6.19 | 161 | 6.26 | 159 | 6.19 | 159 | 6.26 | 159
65 L | 75.2 | 76 | 3.2 | 10 | 5.71 | 175 | 5.83 | 171 | 5.17 | 171 | 5.83 | 171 | 84 | 69
M | 75.3 | 76.6 | 3.6 | 9 | 6.42 | 155 | 6.54 | 153 | 6.42 | 153 | 6.54 | 153
H | 75.3 | 76.6 | 4.5 | 7 | 7.93 | 126 | 8.05 | 124 | 7.93 | 124 | 8.05 | 124
80 L | 87.9 | 88.7 | 3.2 | 10 | 6.72 | 149 | 6.89 | 145 | 6.72 | 145 | 6.89 | 145 | 98 | 75
M | 88 | 89.5 | 4 | 8 | 8.36 | 119 | 8.53 | 117 | 8.36 | 117 | 8.53 | 117
H | 88 | 89.5 | 4.8 | 6 | 9.9 | 101 | 10.1 | 96 | 9.9 | 96 | 10.4 | 96
100 L | 113 | 113.9 | 3.6 | 9 | 9.75 | 102 | 10 | 100 | 9.75 | 100 | 10 | 100 | 124 | 87
M | 113.1 | 115 | 4.5 | 7 | 12.2 | 82 | 12.5 | 80 | 12.2 | 80 | 12.5 | 80
H | 113.1 | 115 | 5.4 | 5 | 14.5 | 69 | 14.8 | 67 | 14.5 | 67 | 14.8 | 67
125 M | 138.5 | 140.8 | 4.8 | 6 | 15.9 | 63 | 16.4 | 61 | 15.9 | 61 | 16.4 | 61 | 151 | 96
H | 138.5 | 140.8 | 5.4 | 5 | 17.9 | 56 | 18.4 | 54 | 17.9 | 54 | 18.4 | 54
150 M | 163.9 | 166.5 | 4.8 | 6 | 18.9 | 53 | 19.5 | 51 | 18.9 | 51 | 19.5 | 51 | 178 | 96
H | 163.9 | 166.5 | 5.4 | 5 | 21.3 | 47 | 21.9 | 45 | 21.3 | 45 | 21.9 | 45
TOLERENCES
a) Thickness
1. Light Tubes |  |  | + Not Limited
-8%
2. Medium and Heavy Tubes |  |  | + Not Limited
-10%
b) Weight
1. Single Tube |  |  | +10%
( Light Series ) |  |  | -8%
2. Single Tube |  |  | +/-10%
( Medium and Heavy Series )
3. For Light Series |  |  | +/-5%
4. For Quantities per load +/-7.5% of 10 tonnes minimum ( Medium and Heavy Series )
c) Length |  |  | 4 to 7 meters unless otherwise specified
d) Tensile Strenght |  |  | -320 | mpa ( min)
e) % of elongation |  | - 20% (min)

## LARGE BORE PIPES
WELDED
ERW LINE PIPE CONFORMING TO API 5L, IS:1978, IS1979
WATER GAS & SEWAGE LINE CONFORMING TO IS 3589
WATER WELL CASING CONFORMING TO IS:4270
DIMENSION AND WEIGHT (KG/M) / (lb/ft)
W.T | [9 empty] | OUTSIDE DIAMETER inch/mm
| Inch | 6.5/8 |  | 8.5/8 |  | 10.3/4 |  | 12.3/4 |  | 14 |  | 16 |  | 16.5 |  | 16.3/4 |  | 18 |  | 18.5/8 |  | 20 |  | 20.7/8
| mm | 168.3 |  | 219.1 |  | 273.1 |  | 323.9 |  | 355.6 |  | 406.4 |  | 419 |  | 426 |  | 457 |  | 473 |  | 508 |  | 530
mm | Inch | Kg/m | lb/ft | Kg/m | lb/ft | Kg/m | lb/ft | Kg/m | lb/ft | Kg/m | lb/ft | Kg/m | lb/ft | Kg/m | lb/ft | Kg/m | lb/ft | Kg/m | lb/ft | Kg/m | lb/ft | Kg/m | lb/ft | Kg/m | lb/ft
3.2 | 0.125 | 13.03 | 8.69 | 17.04 | 11.36 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
3.6 | 0.141 | 14.62 | 9.77 | 19.13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
4 | 0.156 | 16.21 | 10.79 | 21.22 | 14.12 | 26.54 | 17.67 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
4.4 | 0.172 | 17.78 | 11.87 | 23.29 | - | 29.15 | - | 34.67 | 23.13 | 38.1 | - | 43.62 | - | 44.98 | - | 45.74 | - | 49.1 | - | 50.84 | - | - | - | - | -
4.5 | 0.18 | 18.18 |  | 23.81 | - | 29.8 | - | 35.44 | - | 38.96 | - | 44.6 | - | 46 | - | 46.77 | - | 50.21 | - | 51.99 | - | - | - | - | -
4.8 | 0.188 | 19.35 | 12.94 | 25.37 | 16.96 | 31.76 | 21.23 | 37.77 | 25.25 | 41.52 | 27.76 | 47.54 | 31.78 | 49.03 | - | 49.86 | - | 53.53 | 35.8 | 55.42 | - | 59.56 | - | 62.17 | -
5.2 | 0.203 | 20.91 | 13.94 | 27.43 | 18.28 | 34.35 | 22.89 | 40.87 | 27.23 | 44.93 | 29.94 | 51.45 | 34.28 | 53.06 | - | 53.96 | - | 57.93 | - | 59.99 | - | 64.47 | - | 67.3 | -
5.3 | 0.209 | - | - | - | - | - | - | - | - | 45.78 | 30.96 | - | - | - | - | - | - | - | - |  | - | - | - | - | -
5.4 | 0.21 | 21.69 |  | 28.45 | - | 35.64 | - | 42.41 | - | 46.63 |  | 53.4 | - | 55.08 | - | 56.01 | - | 60.13 | - | 62.27 | - | 66.93 | - | 69.86 | -
5.6 | 0.219 | 22.47 | 15 | 29.48 | 19.68 | 36.94 | 24.65 | 43.96 | 29.34 | 48.33 | 32.26 | 55.35 | 36.95 | 57.09 | - | 58.05 | - | 62.34 | 41.63 | 64.54 | - | 69.38 | 46.31 | 71.42 | -
6 | 0.236 | 24.01 | - | 31.53 | - | 39.52 | - | 47.04 | - | 51.73 | - | 59.24 | - | 61.11 | - | 62.14 | - | 66.73 | - | 69.1 | - | 74.27 | - | 77.53 | -
6.3 | 0.248 | 25.17 | - | 33.06 | - | 41.45 | - | 49.34 | - | 54.26 | - | 62.16 | - | 64.11 | - | 65.2 | - | 70.2 | - | 72.5 | - | 77.94 | - | 81.36 | -
6.4 | 0.25 | 25.55 | 17.04 | 33.57 | 22.38 | 42.09 | 28.06 | 50.11 | 33.41 | 55.11 | 36.75 | 63.13 | 42.09 | 65.12 | - | 66.22 | - | 71.12 | 47.44 | 73.64 | - | 79.16 | 52.78 | 82.64 | -
7 | 0.277 | 27.84 | - | 36.61 | 24.72 | 45.93 | - | 54.7 | - | 60.17 | - | 68.94 | - | 71.12 | - | 72.33 | - | 77.68 | - | 80.44 | - | 86.48 | - | 90.28 | -
7.1 | 0.28 | 28.22 | 18.99 | - | - | 46.57 | 31.23 | 55.47 | 37.46 | 61.02 | 41.21 | 69.91 | 47.22 | 72.12 | - | 73.34 | - | 78.77 | 53.23 | 81.57 | - | 87.7 | 59.23 | 91.55 | -
7.8 | 0.307 | - | - | - | - | 51.03 | 34.27 | - | - | - | - | - | - | 79.1 | - | 80.44 | - | - | - | 89.48 | - | - | - | 100.44 | -
7.9 | 0.312 | 31.25 | 21.06 | 41.14 | 27.73 | - | - | 61.56 | 41.48 | 67.74 | 45.65 | 77.63 | 52.32 | 80.09 | - | 81.45 | - | 87.49 | 58.99 | 90.61 | - | 97.43 | 65.66 | 101.71 | -
8 | 0.315 | 31.62 | - | 41.6 | - | 52.3 | - | 62.32 | - | 68.57 | - | 78.59 | - | 81.08 | - | 82.46 | - | 88.58 | - | 91.73 | - | 98.64 | - | 102.98 | -
8.2 | 0.322 | 32.37 | - | 42.65 | 28.58 | 53.56 | - | 63.84 | - | 70.25 | - | 80.52 | - | 83.07 | - | 84.48 | - | 90.75 | - | 93.99 | - | 101.06 | - | 105.51 | -
8.4 | 0.33 | - | - | - | - | - | - | 65.35 | 43.81 | - | - | - | - | 85.05 | - | 86.5 | - | - | - | 96.24 | - | - | - | 108.05 | -
8.7 | 0.344 | 34.24 | 23.1 | 45.14 | 30.45 | 56.72 | 38.27 | 67.62 | 45.62 | 74.42 | 50.22 | 85.32 | 57.57 | 88.03 | - | 89.53 | - | 96.18 | 64.93 | 99.61 | - | 107.12 | 72.28 | 111.84 | -
9 | 0.354 | 35.35 | - | 46.63 | - | 58.61 | - | 69.89 | - | 76.92 | - | 88.2 | - | 90.99 | - | 92.55 | - | 99.43 | - | 102.98 | - | 110.75 | - | 115.63 | -
9.3 | 0.365 | - | - |  | - | 60.5 | 40.52 | - | - | - | - | - | - | 93.96 | - | 95.56 | - | - | - | 106.34 | - | - | - | 119.42 | -
9.5 | 0.375 | 37.2 | 25.05 | 49.1 | 33.07 | 61.75 | - | 73.65 | 49.61 | 81.08 | 54.62 | 92.98 | 62.64 | 95.93 | - | 97.57 | - | 104.84 | 70.65 | 108.58 | - | 116.78 | 78.67 | 121.94 | -
10 | 0.394 | 39.04 | - | 51.56 | - | 64.88 | - | 77.4 |  | 85.22 |  | 97.75 |  | 100.86 | - | 102.58 | - | 110.23 | - | 114.17 | - | 122.8 | - | 128.23 | -
10.3 | 0.405 | 40.13 | - | 53.03 | - | 66.75 | - | 79.65 | 53.57 | 87.7 | 59 | 100.61 | 67.68 | 103.81 | - | 105.59 | - | 113.46 | 76.36 | 117.52 | - | 126.41 | 85.04 | 132 | -
10.5 | 0.413 | 40.86 | - | 54.02 | - | 67.99 | - | 81.15 |  | 89.36 |  | 102.51 |  | 105.77 | - | 107.58 | - | 115.61 | - | 119.75 | - | 128.82 | - | 134.51 | -
11 | 0.432 | 42.67 | 28.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
11.1 | 0.438 | 43.02 | - | 56.94 | 38.33 | 71.72 | 48.28 | 85.62 | 57.65 | 94.3 | 63.5 | 108.2 | 72.86 | 111.65 | - | 113.57 | - | 122.05 | 82.23 | 126.43 | - | 136.01 | 91.59 | 142.03 | -
11.3 | 0.445 | 43.75 | - | 57.9 | - | 72.95 | - | 87.1 | - | 95.94 | - | 110.1 | - | 113.61 | - | 115.56 | - | 124.2 | - | 128.65 | - | 138.41 | - | 144.54 | -
11.5 | 0.453 | 44.47 | - | 58.87 | - | 74.19 | - | 88.59 | - | 97.58 | - | 111.99 | - | 115.56 | - | 117.55 | - | 126.34 | - | 130.87 | - | 140.8 | - | 147.04 | -
11.9 | 0.469 | 45.9 | - | 60.8 | - | 76.65 | - | 91.56 | - | 100.86 | 67.84 | 115.77 | 77.87 | 119.46 | - | 121.52 | - | 130.62 | 87.89 | 135.31 | - | 145.58 | 97.92 | 152.04 | -
12 | 0.472 | 46.25 | - | 61.28 | - | 77.26 | - | 92.3 | - | 101.68 | - | 116.71 | - | 120.43 | - | 122.51 | - | 131.68 | - | 136.42 | - | 146.78 | - | 153.29 | -
12.5 | 0.492 | 48.03 | - | 63.68 | - | 80.33 | - | 95.99 | - | 105.76 | - | 121.42 | - | 125.3 | - | 127.46 | - | 137.02 | - | 141.95 | - | 152.74 | - | 159.52 | -
12.7 | 0.5 | 48.73 | 32.74 | 64.64 | 43.43 | 81.55 | 54.79 | 97.46 | 65.48 | 107.39 | 72.16 | 123.3 | 82.85 | 127.25 | - | 129.44 | - | 139.15 | 93.54 | 144.16 | - | 155.12 | 104.23 | 162 | -
Note: | 1) Size indicates weight lb/ft respective thickness conform to API 5L, IS:1978 and IS:1979
2) Above sizes confirms several other National and International Standards for Different Applications.